## INSTRUMENTS
Tag No. | P&ID Ref | Rev | Type | Operating Conditions |  |  |  |  | Range / Switch Pt. | Wetted Parts | Electrical Details |  |  |  | Installation |  | Control Details |  | Maker / Model |  | Remarks | Supplier Name | Item Cost | Leadtime Worst Case (Weeks) | Order no later than | Date Required | Purchase Order No. | Date Received | Cable Number |  |  |  | FROM |  |  | TO |  |  | kW/A | Classification |  |  |  | Remarks | Est. Length | Proper cable TYPE and SIZE installed? | Cable LUGS and LABELS OK? | Megger Test @ 500VDC | Point-to-Point Conductivity (W) | Rotation check? | Tested by | Checked / Witness | Approved by Clent | Comments
|  |  |  | Service | Media | Flow (m3/hr) | Press. kPa | Temp. (oC) |  |  | Power Supply | Outputs | Accuracy | IP Rating | TX / Switch | Sensor | Monitor | Interlock | TX / Switch | Sensor | [12 empty] | Description | Module No. | I/C Diag | Description | Module No. | I/C Diag |  | Cores | X-Sect. | Type | Voltage Grade
LT271 | WT1193-M002.1 | 1 | Pressure Transmitter Submersible type | Waste Water Inlet Chamber Level | Raw Effluent | N/A | 0-10 | Ambient | 0-1 metres | SS, PUR, PA | 24VDC LOOP | 4-20 mA | 0.5% | IP68 | Intergral to sensor | Hung submersed from cable on bracket over Channel | Raw Water inlet channel level | LAHH, LAH | Wika LS10 0-0.25 bar |  | 3m cable & breather tube and termination vent box | Wika | 555 | [5 empty] | LT | 271 | C | 01 | PLC |  |  | Submersible Pressure Transmitter |  |  |  | 1 pr | 1.5 (7/0.50) | Olex Dekoron overall screened pairs | V90- HT PVC 300VAC 13A | 4-20mA control signal cable. Near inlet screen | 60
Note on B1: The Drawing number of the P&ID that this item appears
Note on C1: P&ID Revision
Note on D1: The type of Instrument Eg. "Pressure / Flow / Level / Conductivity / pH / Temperature / Turbidity / Variable Area" and "Gauge / Meter / Switch / Indicator / Indicating Transmitter"
Note on E2: The purpose of this instrument. Eg. "Raw Water Conductivity", "Clear Water High Level Switch", "Filter Differential Pressure", "CIP Tank Level", "Treated Water Turbidity"
Note on F2: The media that will run through this item. Eg. "Raw Water", "Brine", "Antiscalant" "Diluted Chlorine", "Permeate", "Saturated Air", "Clearwater"
Note on G2: Maximum Design Flow
Note on H2: Maximum Design Pressure
Note on I2: Maximum & if applicable Minimum Design Temperature
Note on P2: How is the Transmitter / Switch Mounted? Eg. "Intergral to Sensor", "Mounted to Wall", "Pipe Mounting Kit"
Note on Q2: How is the Sensor Mounted? Eg. "Bottom entry screwed to pipe", "1" BSP", "Screwed to pipe", "Flange mounted", "Screwed into socket on tank wall"
Note on W1: Supplier Name
Note on X1: Supplier Name
Note on Y1: The longest delivery time quoted by Supplier
Note on Z1: Latest Date to order item to meet project deadlines
Note on AA1: Date Required by Project
Note on AB1: WTA Purchase Order Number
Note on AC1: Date Received item