## Version
1.0 | Initial draft
1.1 | Release, added columns for ITP/SAT
1.2 | Minor mods during FAT
1.3 | Minor mods during SAT

## Digital Inputs
DNP | Point Name | Type | Class | UNSOL | State 0 | State 1 | IO Src | Chan | SMS | History | ITP/SAT RTU | ITP/SAT SCADA
0 | HL P1 Running | PHY | 1 | Y | Not Running | Running | ONBOARD | 0 |  | Y | Y | Y
1 | HL P1 Fault | PHY | 1 | Y | Healthy | Fault | ONBOARD | 1 | Y | Y | Y | Y
2 | HL P2 Running | PHY | 0 | Y | Not Running | Running | ONBOARD | 2 |  | Y | Y | Y
3 | HL P2 Fault | PHY | 1 | Y | Healthy | Fault | ONBOARD | 3 | Y | Y | Y | Y
4 | CW High Float Alarm | PHY | 1 | Y | Alarm | Healthy | ONBOARD | 4 | Y | Y | Y | Y
5 | Battery Low | PHY | 1 | Y | Alarm | Healthy | ONBOARD | 5 | Y | Y | Y | Y
6 | Phase Fail | PHY | 1 | Y | Fault | Healthy | ONBOARD | 6 | Y | Y | Y | Y
7 | Mains Fail | PHY | 1 | Y | Fault | Healthy | ONBOARD | 7 | Y | Y | Y | Y
8 | CW Low Float Alarm | PHY | 1 | Y | Alarm | Healthy | ONBOARD | 8 | Y | Y | Y | Y
9 | RW FM Pulse | PHY | 0 |  | No Pulse | Pulse | ONBOARD | 9 |  |  | Y | Y
10 | CW FM Pulse | PHY | 0 |  | No Pulse | Pulse | ONBOARD | 10 |  |  | Y | Y
11 | CW Turbidity Alarm | PHY | 1 | Y | Healthy | Alarm | ONBOARD | 11 | Y | Y | Y | Y
12 | Chlorine Leak AlarmB | PHY | 1 | Y | Healthy | Alarm | ONBOARD | 12 | Y | Y | Y | Y
13 | Chlorine Leak AlarmA | PHY | 1 | Y | Healthy | Alarm | ONBOARD | 13 | Y | Y | Y | Y
14 | Emergency Supply Available | PHY | 1 | Y | NO | YES | ONBOARD | 14 |  | Y | Y | Y
15 | Site Security Alarm | PHY | 1 | Y | Alarm | Normal | ONBOARD | 15 | Y | Y | Y | Y
16 | Spare | PHY |  |  |  |  | ONBOARD | 16
17 | Spare | PHY |  |  |  |  | ONBOARD | 17
18 | Spare | PHY |  |  |  |  | ONBOARD | 18
19 | Spare | PHY |  |  |  |  | ONBOARD | 19
40 | HL P1 Failed to Start Alarm | DER | 1 | Y | Healthy | Alarm | LOGIC |  |  | Y | Y | Y
41 | HL P2 Failed to Start Alarm | DER | 1 | Y | Healthy | Alarm | LOGIC |  |  | Y | Y | Y
42 | P2P link Failed (with Elevated Res) | DER | 1 | Y | Healthy | Alarm | LOGIC |  |  | Y | Y | Y
44 | HL P1 Not Available | DER | 1 | Y | Healthy | Alarm | LOGIC |  |  | Y | Y | Y
45 | HL P2 Not Available | DER | 1 | Y | Healthy | Alarm | LOGIC |  |  | Y | Y | Y

## Digital Outputs
DNP | Point Name | OP Style | Type | Class | State 0 | State 1 | IO Src | Chan | ITP/SAT RTU | ITP/SAT SCADA
0 | HL Pump1 Stop | DO | PHY | 0 | No Stop | Stop | ONBOARD | 0 | Y | Y
1 | HL Pump1 Start | DO | PHY | 0 | No Start | Start | ONBOARD | 1 | Y | Y
2 | HL Pump2 Stop | DO | PHY | 0 | No Stop | Stop | ONBOARD | 2 | Y | Y
3 | HL Pump2 Start | DO | PHY | 0 | No Start | Start | ONBOARD | 3 | Y | Y
4 | Spare | DO | PHY | 0 |  |  | ONBOARD | 4
5 | Spare | DO | PHY | 0 |  |  | ONBOARD | 5
6 | Spare | DO | PHY | 0 |  |  | ONBOARD | 6
7 | Spare | DO | PHY | 0 |  |  | ONBOARD | 7
8 | Spare | DO | PHY | 0 |  |  | ONBOARD | 8
20 | Pumps Mode Remote Manual/Manual Off | DO | DER | 0 | Manual | Auto | SCADA |  | Y | Y
21 | HL P1 Remote Manual Start | DO | DER | 0 | Stop | Start | SCADA |  | Y | Y
22 | HL P2 Remote Manual Start | DO | DER | 0 | Stop | Start | SCADA |  | Y | Y
23 | Spare | DO | DER | 0
24 | Call for Water bit RWPS | DO | DER | 0 | OFF | ON | LOGIC |  | Y | Y
25 | Pump 1 in Maintenance | DO | DER | 0 | NO | YES | LOGIC |  | Y | Y
26 | Pump 2 in Maintenance | DO | DER | 0 | NO | YES | LOGIC |  | Y | Y

## Analogue Inputs
DNP | Point Name | IO Type | Class | DNP Type | UNSOL | IO Src | Channel | RawLo | RawHi | EngLo | EngHi | Units | SMS | HISTORY | ITP/SAT RTU | ITP/SAT SCADA
0 | CW Res Level | PHY | 2 | FLOAT | Y | ONBOARD | 0 | 0 |  | 0 | 100 | % | Y | Y | Y | Y
1 | RW Flow | PHY | 2 | FLOAT | Y | ONBOARD | 1 | 0 |  | 0 | 50 | l/s |  | Y | Y | Y
2 | CW Flow | PHY | 2 | FLOAT | Y | ONBOARD | 2 | 0 |  | 0 | 60 | l/s |  | Y | Y | Y
3 | Filter1 Turbidity | PHY | 2 | FLOAT | Y | ONBOARD | 3 | 0 |  | 0 | 500 | NTU |  | Y | Y | Y
4 | Filter2 Turbidity | PHY | 2 | FLOAT | Y | ONBOARD | 4 | 0 |  | 0 | 500 | NTU |  | Y | Y | Y
5 | Clarifier Sludge Depth | PHY | 2 | FLOAT |  | ONBOARD | 5 | 0 |  | 0 |  | mm |  | Y | Y | Y
6 | Chlorine Residual | PHY | 2 | FLOAT | Y | ONBOARD | 6 | 0 |  | 0 |  | mg/L | Y | Y | Y | Y
7 | Treated Water pH | PHY | 2 | FLOAT | Y | ONBOARD | 7 | 0 |  | 0 | 14.2 | pH |  | Y | Y | Y
20 | RW Flow Total | DER | 2 | DINT | Y | LOGIC |  | 0 |  | 0 |  | kL |  | Y | Y | Y
21 | CW Flow Total | DER | 2 | DINT | Y | LOGIC |  | 0 |  | 0 |  | kL |  | Y | Y | Y
22 | CW Res Level in meters | PHY | 2 | FLOAT | Y | LOGIC | 0 | 0 |  | 0 | 100 | m |  | Y | Y | Y

## Analogue Outputs
DNP | Point Name | IO Type | Class | DNP Type | IO Src | Channel | EngLo | EngHi | Units | HISTORY | ITP/SAT RTU | ITP/SAT SCADA
20 | High High Level Setpoint for Clear Water | DER | LOCAL | FLOAT | SCADA |  | 0 | 150 | % | Y | Y | Y
21 | Low Low Level Setpoint for Clear Water | DER | LOCAL | FLOAT | SCADA |  | 0 | 150 | % | Y | Y | Y
22 | Control High Level Setpoint for Clear Water | DER | LOCAL | FLOAT | SCADA |  | 0 | 150 | % | Y | Y | Y
23 | Control Low Level Setpoint for Clear Water | DER | LOCAL | FLOAT | SCADA |  | 0 | 150 | % | Y | Y | Y
24 | Control High Level Setpoint for Elevated Res | DER | LOCAL | FLOAT | SCADA |  | 0 | 150 | % | Y | Y | Y
25 | Control Low Level Setpoint for Elevated Res | DER | LOCAL | FLOAT | SCADA |  | 0 | 150 | % | Y | Y | Y
26 | Watchdog Frequency SP RWPS | DER | LOCAL | FLOAT | SCADA |  | 0 | 999 | sec | Y | Y | Y